## Revision, License & Use
Revision History
Date | Version | Description
2019-12-23 | 0.1 | First draft for evaluation
2020-01-10 | 0.25 | Updated draft in compliancy checklist pump section
2022-07-28 | 1 | Reference for Cold Plate Requirements Doc Sub-WG
2022-07-28 | 2 | Working document for Cold Plate Requirements Rev 2 Sub-WG
This work is licensed under a Creative Commons Attribution 4.0 International License.

## Compliancy Checklist
CONTRIBUTION NAME
CONTRIBUTING MEMBER/COMPANY
ADDRESS
CITY, STATE ZIP
COUNTRY
COMPANY CONTACT/ Email:
Refer to the OCP Cold Plate Requirements document for qualification criteria
https://docs.google.com/document/d/1HR5O_bPcgpcjhEMGIejJ6hUor7DDx6_ek6bzvKcc7X8/edit?usp=sharing
Notes:
Chapter 4: Technology definitions | Description | Check which applies
Technology domain | Technology Cooling System (TCS) | FALSE
Liquid type | Single-phase | FALSE
| Two-phase | FALSE
Wetted materials | Compatbility determined between liquid cooling solution and cooling liquid | FALSE
Chapter 5: Cooling Components Selection and Parameters of Importance | Description | Check which applies
Cooling Liquid | Water with Additives | FALSE
| Glycol Based Liquids | FALSE
| Dielectric | FALSE
| Refrigerants | FALSE
| Parameters of Importance (Spreadsheet tab filled out) | FALSE
Cold Plate | Micro-channel cold plate | FALSE
| Other: describe | FALSE
| Parameters of Importance (Spreadsheet tab filled out) | FALSE
Coolant Distribution Unit (CDU) | In-Rack | FALSE
| Row Level | FALSE
| Parameters of Importance (Spreadsheet tab filled out) | FALSE
Rack Manifold | Manifold location: Front of Rack | FALSE
| Manifold Location: Rear of Rack | FALSE
| Manifold Location: Side of Rack | FALSE
| Parameters of Importance (Spreadsheet tab filled out) | FALSE
Quick Disconnect Couplings | Shutoff feature | FALSE
| Hand mate QD | FALSE
| Blind mate QD | FALSE
| Parameters of Importance (Spreadsheet tab filled out) | FALSE
Pump | In-Rack in assist configuration | FALSE
| In-IT Equipment in assist configuration | FALSE
| Redundant pumps in parallel configuration | FALSE
| Redundant pumps in in-line/series configuration | FALSE
| Parameters of Importance (Spreadsheet tab filled out) | FALSE
Chapter 6: Liquid Cooling Requirements | Description | Check which applies
Certification Markings | List all region certification compliancies | (Regional compliancy list)
| List all local certification compliancy | (Local compliance list)
Pressure Safety Requirements | Compliance with IEC 60950-1 | FALSE
| Compliance with IEC 62368-1 | FALSE
| Compliance with ASME B31.3 “Process Piping” (2018) | FALSE
Risk Management | Service and maintenance requirements determined | FALSE
| Redundancy requirements of cooling solution determined | FALSE
| Cooling fluid MSDS & TDS available to anyone in DC | FALSE
| Spill management and absorption materials present to manage a catastrophic spill | FALSE
| Disposal procedures in place for spill/leak management and/or replacement of cooling liquid | FALSE
| Liquid containment strategy complying with local regulations | FALSE
| Gas leakage into the atmosphere is prevented (highly evaporative liquids) | FALSE
| Full health and safety documentation is present | FALSE
| Full action plan for liquid cooling loop and IT equipment if leakage detected | FALSE
Liquid Cooling Classifications | IT Equipment: Hybrid Basic | FALSE
| IT Equipment: Hybrid Intermediate | FALSE
| IT Equipment: Hybrid Advanced | FALSE
| IT Equipment: Full Liquid | FALSE
| Liquid Cooled Ready Rack without Door Heat Exchanger | FALSE
| Liquid Cooled Ready Rack with Door Heat Exchanger | FALSE
Sensor Requirements | Minimum Sensor Requirements | FALSE
| Advanced Sensor Requirements | FALSE
| Use of DMTF Redfish | FALSE
Leakage Detection | Indirect | FALSE
| Direct | FALSE
Leakage Intervention | Manual | FALSE
| Automatic | FALSE
Comparison Metrics | Spreadsheet tab filled out (ComparisonMetrics) | FALSE

## ParametersOfImportance
Single-phase cold plate | Value
Parameter | Metric
Heat transfer performance | W/m² °C or °C/W
Operating pressure | Pa
Pressure drop | PQ Curve
Thermal Resistance | RQ Curve
Height | mm
Active surface area | m2
Filtration requirement | 𝛍m
Flatness | 𝛍m
Stiffness | N/mm
Operating point
Flow rate | L/min
Thermal Resistance | W/m² °C or °C/W
Liquid inlet temperature | °C
Liquid outlet temperature | °C
Wetted Materials | List
Two-phase cold plate (pool boiling) | Value
Parameter | Metric
Heat transfer performance | W/m² °C or °C/W
Operating pressure | Pa
Height | mm
Active surface area | m2
Filtration requirement | 𝛍m
Flatness | 𝛍m
Stiffness | N/mm
Operating points
Flow rate / 100W | L/min
Thermal Resistance | W/m² °C or °C/W
Liquid inlet temperature | °C
Vapor outlet temperature | °C
Vapor outlet quality | %
Wetted Materials | List
Hose/Tubing | Value
Maximum Operating Pressure | kPa
Burst Pressure | kPa
Minimum Operating Temperature | degC
Maximum Operating Temperature | degC
Minimum Bend Radius | mm
Inside Diameter | mm
Outside Diameter | mm
Pressure Drop | kPa/m
Permeation | g/m2/day *(must specify fluid and temp)
Flammability Rating | UL94 classification
Wetted Material
Quick Disconnects | Value
Parameter | Metrics
Flow Rate | L/min, gpm
Flow Coefficient | Kv, Cv
Operating Pressure | Pa
Burst Pressure | Pa, psi
Pressure drop | PQ Curve
Spillage (liquid expunction) | mL
Inclusion (air introduction) | mL
Temperature – Operating, Storage / Shipping | °C
Connection Force | N
Connection Cycles | Mechanical cycles / connect and disconnect
Nominal flow / hydraulic diameter | Mm
Quick Disconnect Style | Blind-mate or hand-mate
Terminations | Barbed, compression style, threaded
Wetted Materials | Compatible
Single-phase cold plate loop | Value
Parameter | Metric
Heat transfer performance | W/m² °C or °C/W
Operating pressure | Pa
Pressure drop | PQ Curve
Thermal Resistance | RQ Curve
Height | mm
Active surface area | m2
Filtration requirement | 𝛍m
Flatness | 𝛍m
Stiffness | N/mm
Operating point
Flow rate | L/min
Thermal Resistance | W/m² °C or °C/W
Liquid inlet temperature | °C
Liquid outlet temperature | °C
Wetted Materials | List
Two-phase cold plate (pool boiling) | Value
Parameter | Metric
Heat transfer performance | W/m² °C or °C/W
Operating pressure | Pa
Height | mm
Active surface area | m2
Filtration requirement | 𝛍m
Flatness | 𝛍m
Stiffness | N/mm
Operating points
Flow rate / 100W | L/min
Thermal Resistance | W/m² °C or °C/W
Liquid inlet temperature | °C
Vapor outlet temperature | °C
Vapor outlet quality | %
Wetted materials | List
Rack Manifold | Value
Parameter | Metric
Total liquid volume | m3
Internal diameter or dimension | mm
Coupling insertion diameter | mm
Height | mm
Width | mm
Depth | mm
Weight | kg
Manifold rack extrusion into white space | None (in-rack) or Extrusion (location and m2)
TCS liquid connector style and dimension | mm (e.g. Blind-mate, hand-mate, threaded)
TCS connection location | Top or foot of rack
Maximum rated pressure | Pa
Maximum liquid flow rate | L/min
Number of ports
Spacing between ports | U or OU
Air-bleed valve | Location, operation specification
Wetted Materials | List
Coolant Distrubution Units | Value
Parameter | Metric
Maximum cooling capacity @ 4˚C Approach | kW1
Total liquid volume | m3
Approach Temperature Curve | ˚C
Acoustic sound power or sound pressure | BA or dBA
System Pressure Flow Rate Curve | Pa vs L/min
Width | mm
Depth | mm
Weight | kg
Power draw and variable load capabilities | kVa at specific voltage and add variable load metrics
TCS liquid connector style and dimension | mm (e.g. Blind-mate, hand-mate, threaded)
TCS connection location | Top or foot of rack
FWS liquid connector style and dimension | mm (e.g. Blind-mate, hand-mate, threaded)
FWS connection location | Top or foot of rack

## ComparisonMetrics
Chapter 6
Classification | Metrics | Notes
IT equipment width | 19’’ or 21’’
Rack Width | inches or mm (24’’/600 mm) or custom
Rack height | U
Rack depth | m (1.1 and 1.2 m) or custom
Rack service area - Back | m x m
Rack service area - Front | m x m
Wall Power/rack | kW/rack
IT equipment chassis height (i.e., server, blade) | U (1U, 2U, any U, custom)
Fully loaded rack weight (i.e., rack with IT equipment and cooling liquid) | Kg
Manifold location | Manifold location
Manifold connector type | Hand-mate, blind-mate
Water with additives, Glycol based, Dielectric, Refrigerants
With or without door heat exchanger
IT equipment cooling classification | Basic hybrid, intermediate hybrid, full liquid
Maximum TCS cooling liquid supply temperature to racks | oC Can be based on the facility cooling liquid max temperature according to ASHRAE’s definitions (W1: 17 oC, W2: 27 oC, W3: 32 oC, W4: 45 oC, W5 > 45 oC) + temperature rise over the CDU
Maximum TCS cooling liquid return temperature from racks | oC
Coolant Distribution Unit (CDU) | In-rack, In-Row, Facility (and dimensions of the CDU)
#
Maximum cooling capacity @ 4˚C Approach | kW [1]
CDU Power Consumption at full load | W
Total cooling subsystem (fan/pump) power/rack | W
Total power subsystem losses/rack | W
Total power into the compute components | # W (including CPUs, GPUs, Memory, Storage, Networking)
Maximum allowable pressure on TCS side | # Pa
Maximum allowable pressure on FWS side | # Pa
Maximum pressure drop on TCS side | # Pa
Maximum pressure drop on facility cooling liquid side | # Pa
Maximum CDU TCS flow rate | # l/s
Maximum CDU facility cooling liquid flow rate | # l/s
Leak Detection | Indirect/Direct
Leak Mitigation | Manual/Automatic
[1] Liquids used in primary and secondary must be listed.