## Slide 2: Data Center Electrical Spec for System Stability Melaku Mihret, Electrical Engineer, Facebook
DATA CENTER FACILITIES

## Slide 3: Why the Spec for System Stability?
Ensure electrical system stability by design
Address end-to-end system requirement
Minimize voltage unbalance
Notes: Defines limits for all passive electrical components
Provide impedance measurement guideline

## Slide 4: Main Switchboard (MSB) Currents
4000
-4000
000
0
-2000
Phase A
Phase B
Phase C
Current (A)
400 ms
100 ms
1 s
100 ms
100 ms
100 ms
200 ms
0 ms
100 ms
2s
100 ms
600 ms
800 ms
Notes: Instability and resonance at multiple sites
System resonance at 71 Hz leads to high harmonics in current
Instability and resonance at multiple sites
System resonance at 71 Hz leads to high harmonics in current
Nonlinear coupling through converter generates additional harmonic at 49 Hz (71+49=2×60)

## Slide 5: Origin of the Resonance
May 2017
June 2017
July 2017
August 2017
Total MSB Load (kW)
MSB Neutral Current (A)
April 2017
MSB Neutral Current Spikes
2000
1000
0
1600
The impedance interaction between the building electrical system and the power supplies are the root cause.
Notes: Root cause - impedance interaction between the building electrical system and the power supplies
Also observed huge spike on the power and the neutral current at higher power.
Nonlinear coupling through converter generates additional harmonic at 49 Hz ()
Root cause - impedance interaction between the building electrical system and the power supplies
Also observed huge spike on the power and the neutral current at higher power.
Nonlinear coupling through converter generates additional harmonic at 49 Hz (71+49=2×60)

## Slide 6: Simplified Electrical System
PTX
MVS
MSB
Busway
SB
Normal Path
Reactor
Utility
Substation
G
PSU
RPP
G
MSB Bypass
SB-RPP Bypass
Notes: Multiple redundancy paths

## Slide 7: Impedance Analysis
Utility
Substation
G
PSU
G
Reactor
RPP
Zl(s)
Zs(s)
Zs(s)
Zl(s)
Single-phase equivalent circuits,
one in each sequence
Three-phase power distribution system
Notes: Three-phase power distribution system
Reduction to three single-phase equivalences based on symmetrical component theory
We need to find a we to determine the equivalent impedance of the complex system

## Slide 8: Equivalent Building Impedance
Nonhomogeneous Loading
L0
PSUs on reserve MSB
Utility
L1
PSU
L2
PSU
PSUs on each MSBs
MSBs per reserve
L2
PSU
PSU
Ls
Notes: System Stability can be Determined by Testing one PSU Against a Source with Output Impedance Defined by
Applied scaling on the impedances
The equivalent source inductance are computed based on the maximum eigenvalues of the loop gain
System Stability can be Determined by Testing one PSU Against a Source with Output Impedance Defined by 𝐿_𝑠

## Slide 9: Base Impedance Ratio (BIR)
The system is more stable if:
Building inductance is small
Power supply input impedance is large
BIR is the ratio of PSU to building impedance
Data Center Building
Power Supply
Zs
Zl
Notes: BIR is the ratio of PSU to building impedance.
Lower building impedance is better for stability.
The higher the operating voltage, the better.

## Slide 10: Building Requirement
Base Impedance Ratio | Conclusion
> 2.5 | Pass
2.0 – 2.5 | Marginal Pass
1.5 – 2.0 | Marginal Fail
< 1.5 | Fail
Notes: Field impedance measurement from multiple sites
Testing the PSUs with equivalent inductors

## Slide 11: Power Supply Requirement
Base Impedance Ratio | Conclusion
> 2.0 | Fail
1.5 – 2.0 | Marginal Fail
1.0 – 1.5 | Marginal pass
< 1.0 | Pass
Notes: Field impedance measurement from multiple sites
Testing the PSUs with equivalent inductors

## Slide 12: Site Impedance Measurement
Fort Worth, TX
Altoona, IA
Clonee, Ireland
Los Lunas, NM
New Albany, OH
Ashburn, VA

## Slide 13: Data Center Impedance Measurement
Device
Under
Test
a
b
c
n
Shorting Wire
High Current Injection Wire
+
-
Isource
Vmeas
Notes: We measure the impedance of every segment in the low voltage distribution system.
We test at various frequencies
We compute the utility and substation transformer impedances.

## Slide 14: Software Modeling
Phase A
Phase B
Phase C
Racks Input Current
Stable rack currents
Irms (A)
Time (s)
Phase A
Phase B
Phase C
Racks Input Voltage
Stable rack voltages
Vrms (V)
Time (s)
Notes: Models built in and simulations performed with ANSYS Simplorer

## Slide 15: Model with Failed PSU
Unstable rack voltages
Phase A
Phase B
Phase C
Racks Input Voltages
Vrms (V)
Time (s)
Unstable rack currents
Racks Input Currents
Irms (A)
Time (s)
Phase A
Phase B
Phase C
Unstable rack currents
Unstable rack voltages

## Slide 16: Impedance Spec
The spec ensures system stability by design
Specify the maximum inductance limit
Applies to all passive electrical components - Switchboards, Reactors, Busways and Cables
 | Main Switchboard | Reactor | Busway
Average self-inductance | 12.0 µH | 65.0 µH | 13.0 µH
Self-inductance deviation | 3.0 µH | 1.0 µH | 1.5 µH
Average mutual inductance | 6.5 µH | 1.0 µH | 7.5 µH
Examples of the Spec
We are engaging vendors to meet this spec and to develop a process of impedance testing
Notes: The spec is defined based on three key parameters, average self and mutual inductance determines the stability; inductance deviation defines the voltage unbalance.
Specify the maximum inductance limit for each passive electrical component
These components include: MSBs, SBs, RPPs, Agg Reactors, PDUs, STCs and Cables
Started vendor engagement

## Slide 17: Impedance Composition
Chart: 
| PTXR | Cable (PTXR-MSBR) | MSBR | Cable (MSBR-SBR) | Agg Reactor | SBR | Cable (SBR-RPP) | Busway
 | 8465.3696 | 8140.8 | 11712 | 4876.8 | 22012.8 | 4252.8 | 4145.28 | 531.6
Notes: MSB and PTX contribute the most inductance in the normal path
Agg Reactor and MSB the dominance impedance contributors in row reserve loop

## Slide 18: Main Switchboard Comparison
Chart: Inductance from multiple vendors
| Vendor 5 | Vendor 2 | Vendor 2 | Vendor 1 | Vendor 1 | Vendor 3 | Vendor 4
Average Self L (µH) | 10.3333 | 15.51 | 16.58 | 10.53 | 10.7333 | 8.8333 | 9.2667
Spec
Fail
Pass
Inductance (µH)
Notes: We analyzed and compared 5 switchboard vendors and integrators, compared with the spec limit
1 Vendor failed the inductance limit

## Slide 19: Main Switchboard Comparison
Chart: Mutual Inductance from multiple vendors
| Vendor 5 | Vendor 2 | Vendor 2 | Vendor 1 | Vendor 1 | Vendor 3 | Vendor 4
Average mutual Inductance L (µH) | 6.845 | 10.33 | 10.33 | 5.9283 | 4.85 | 5.6167 | 5.5333
Spec
Inductance (µH)
Notes: 3 vendors passed the mutual inductance limit

## Slide 20: Main Switchboard Comparison
Chart: Inductance deviation from multiple vendors
| Vendor 5 | Vendor 2 | Vendor 2 | Vendor 1 | Vendor 1 | Vendor 3 | Vendor 4
Inductance Deviation (µH) | 0.30667 | 2.76 | 2.73 | 1.99 | 1.7333 | 0.13333 | 2.4667
Spec
Inductance (µH)
Notes: Inductance deviation derives the voltage unbalance
All vendors pass this spec

## Slide 21: How to Improve System Stability?
Notes: Reduce the building impedance
Increase PSU input impedance – a lot of work with PSU vendors. Also there is an OCP presentation

## Slide 22: Zero Sequence is the Weakest Link
PTX
MVS
MSB
Busway
SB
Reactor
Utility
Substation
G
PSU
RPP
G
Delta Configuration is better for zero-sequence stability
Delta Configuration
Notes: Zero-sequence impedance is the weakest link

## Slide 23: Increase Phase-Neutral Coupling
203 |  | 
 | 242 | 
 |  | 199
Zero-Sequence Inductance = 533 nH/m
Zero-Sequence Inductance = 286 nH/m
Existing cable bus
Proposed cable bus
130 |  | 
 | 131 | 
 |  | 131
Inductance in nH/m
Inductance in nH/m
Phase arrangement is key to reduce cable impedance
A
B
C
A
B
C
C
B
A
N
N
N
N
N
N
B
B
C
C
A
A
B
C
A
A
B
C
A
B
C
C
B
A
N
N
N
N
N
N
B
B
C
C
A
A
B
C
A
Notes: Improve system stability by reducing the impedance
Reduce zero-sequence inductance by half

## Slide 24: Utilize Phase Coupling
Three-Phase core reactor
Single-Phase core reactor
Inductance (µH) |  | 
60.9 | -11.9 | -11.9
-11.9 | 60.2 | -11.9
-11.9 | -11.9 | 61.5
Inductance (µH) |  | 
60.9 | 0.5 | 0.6
0.6 | 60.2 | 0.6
0.5 | 0.5 | 61.5
3-phase core reactors are better for system stability than reactors with 3 single-phase cores
Zero-Sequence BIR
2.57
Zero-Sequence BIR
2.28
Notes: Negative mutual inductance reduces the zero-sequence
Zero-sequence impedance is the weakest link

## Slide 25: Contributors
Dr. Jian Sun, Professor, Rensselaer Polytechnic Institute
Morris Toporek, DCD, Facebook
Greg Epstein, SE&D, Facebook
Debra Vieira and Mike Tu, FacEng, Facebook
Hamid Keyhani, Ted Tang and David Sun, Hardware Eng, Facebook

## Slide 26: Call to Action
https://www.opencompute.org/projects/data-center-facility